## TestPlan
0.0,0.1,0.0,0.3,0.1,0.2,0.0 |  |  | 2) Configure Definitions sheet |  |  | 3) Save as TestLogSummer01.xlsx {Summer ¦ Winter} {01 ¦ 02 ¦ …} Season and priority code
Operator | DG Code | P3ph (B2) [kW] | Pwall (B1) [kW] | Pgen [kW] | Penetration [%] | RLC [kW] | GE Amp RTDS File | QC load [kVAr] | PF load [] | LabView File Nums | Normal? | Comment
2015-06-17
| xoff a | 0 | 31.2 | 31.2 | 26.15% | 119.3 | n/a | -8.212 | 0.95 |  | s | LimRTDS=0.96, Local Var Ref = -8000, No Passive Cap
| xoff b | 0 | 42.8 | 42.8 | 35.88% | 119.3 | n/a | -8.212 | 0.95 | 252-253 | y | Characteristics similar to MotorD in most cases
| x45 a | 42 | 31.2 | 73.2 | 61.36% | 119.3 | n/a | -8.212 | 0.95 | 250-251 | y
| x45 c | 42 | 53.4 | 95.4 | 79.97% | 119.3 | n/a | -8.212 | 0.95 | 248-249 | y
| x100 b | 76 | 42.8 | 118.8 | 99.58% | 119.3 | n/a | -8.212 | 0.95 | 246-247 | y
| x100 c | 76 | 53.4 | 129.4 | 108.5% | 119.3 | n/a | -8.212 | 0.95 | 244-245 | y
| x100 d | 76 | 62.4 | 138.4 | 116% | 119.3 | n/a | -8.212 | 0.95 |  | s
| xoff a | 0 | 31.2 | 31.2 | 26.15% | 119.3 | n/a | 6.7751 | 0.98 |  | s | LimRTDS=0.96, Local Var Ref = 6800, No Passive Cap
| xoff b | 0 | 42.8 | 42.8 | 35.88% | 119.3 | n/a | 6.7751 | 0.98 | 262-263 | y
| x45 a | 42 | 31.2 | 73.2 | 61.36% | 119.3 | n/a | 6.7751 | 0.98 | 260-261 | y
| x45 c | 42 | 53.4 | 95.4 | 79.97% | 119.3 | n/a | 6.7751 | 0.98 | 258-259 | y
| x100 b | 76 | 42.8 | 118.8 | 99.58% | 119.3 | n/a | 6.7751 | 0.98 | 256-257 | y
| x100 c | 76 | 53.4 | 129.4 | 108.5% | 119.3 | n/a | 6.7751 | 0.98 | 254-255 | y
| x100 d | 76 | 62.4 | 138.4 | 116% | 119.3 | n/a | 6.7751 | 0.98 |  | s
| xoff a | 0 | 31.2 | 31.2 | 26.15% | 119.3 | n/a | 31 | 1 |  | s | LimRTDS=0.96, Local Var Ref = 31000, No Passive Cap
| xoff b | 0 | 42.8 | 42.8 | 35.88% | 119.3 | n/a | 31 | 1 | 274-275 | y
| x45 a | 42 | 31.2 | 73.2 | 61.36% | 119.3 | n/a | 31 | 1 | 272-273 | y
| x45 c | 42 | 53.4 | 95.4 | 79.97% | 119.3 | n/a | 31 | 1 | 269-271 | y
| x100 b | 76 | 42.8 | 118.8 | 99.58% | 119.3 | n/a | 31 | 1 | 266-268 | y
| x100 c | 76 | 53.4 | 129.4 | 108.5% | 119.3 | n/a | 31 | 1 | 264-265 | y
| x100 d | 76 | 62.4 | 138.4 | 116% | 119.3 | n/a | 31 | 1 |  | s
| xoff a | 0 | 31.2 | 31.2 | 26.15% | 119.3 | n/a | 55.2249 | 0.98 |  | s | LimRTDS=0.96, Local Var Ref = 55200, No Passive Cap
| xoff b | 0 | 42.8 | 42.8 | 35.88% | 119.3 | n/a | 55.2249 | 0.98 | 284-285 | y
| x45 a | 42 | 31.2 | 73.2 | 61.36% | 119.3 | n/a | 55.2249 | 0.98 | 282-283 | y
| x45 c | 42 | 53.4 | 95.4 | 79.97% | 119.3 | n/a | 55.2249 | 0.98 | 280-281 | y
| x100 b | 76 | 42.8 | 118.8 | 99.58% | 119.3 | n/a | 55.2249 | 0.98 | 278-279 | y
| x100 c | 76 | 53.4 | 129.4 | 108.5% | 119.3 | n/a | 55.2249 | 0.98 | 276-277 | y
| x100 d | 76 | 62.4 | 138.4 | 116% | 119.3 | n/a | 55.2249 | 0.98 |  | s
| xoff a | 0 | 31.2 | 31.2 | 26.15% | 119.3 | n/a | 70.212 | 0.95 |  | s
| xoff b | 0 | 42.8 | 42.8 | 35.88% | 119.3 | n/a | 70.212 | 0.95 |  | s
| x45 a | 42 | 31.2 | 73.2 | 61.36% | 119.3 | n/a | 70.212 | 0.95 |  | s
| x45 c | 42 | 53.4 | 95.4 | 79.97% | 119.3 | n/a | 70.212 | 0.95 |  | s
| x100 b | 76 | 42.8 | 118.8 | 99.58% | 119.3 | n/a | 70.212 | 0.95 |  | s
| x100 c | 76 | 53.4 | 129.4 | 108.5% | 119.3 | n/a | 70.212 | 0.95 |  | s
| x100 d | 76 | 62.4 | 138.4 | 116% | 119.3 | n/a | 70.212 | 0.95 |  | s

## Definitions
119.3 | Utility P [kW] // read from LabView screen
31 | Utility Q inductive [kVAr] // read from Amplifier screen
0.96786 | Actual power factor after rounding QL
113 | P value from Amplifier Screen
29.5 | Q value from LabView Utility Screen
Configure load composition in RTDS and run it on grid voltage (not internal voltage)
118.4 | Enter measured P from the runtime screen into cell A6
34.8 | Ditto for measured Q into cell A7
Disconnect RLC capacitors if any and set the amplifier "Local VAR Ref" = 0
Run GE amplifier without any PV
Adjust LimRTDS to get Utility P approximatelly equal to 120kW. Set that value as the Max value on the slider.
Record Utility P[kW] from Labview into cell A1
Ditto for Utility Q[kVAr] into cell A2
Switch back to TestPlan tab (Sheet)