## TestLogsAll
| Comment | CompCode | DGCode | DirName | FileName | GEAmpP | GEAmpQ | LVFiNums | LabViewP | LabViewQ | NrmlFlg | Operator | P3phB2 | PFload | Pgen | PrcntPen | PwallB1 | QCload | RLCpwr | RTDSFile | RtdsP | RtdsQ | lvComment | lvProgRev | TDMSfname | TDMSfnum | tStart | tEnd | tIslStart | tIslEnd | tIslDur | ix1 | ix1left | ix2 | ix2right | ixflags | fIslStd | fIslMean | fIslMin | fIslMax | fIslSkw
0 | Characteristics similar to MotorD in most cases | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | xoff b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 252-253 | 119.3 | 29.5 | y |  | 0 | 0.95 | 42.8 | 0.35876 | 42.8 | -8.212 | 119.3 | n/a | 118.4 | 34.8 | Summer01, xoff b, 36%Pen, 0.95PF | GE Anti-Island 4a.vi | 0252 06-17-15 11-11.tdms | 252 | 2015-06-17 18:11 | 2015-06-17 18:11 | 0.09235 | 0.115 | 0.02265 | 1847 | 1514 | 2300 | 2366 | 136 | 1.5716 | 60.5483 | 57.5474 | 66.6368 | 1.9259
1 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 a | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 250-251 | 119.3 | 29.5 | y |  | 42 | 0.95 | 73.2 | 0.61358 | 31.2 | -8.212 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 a, 61%Pen, 0.95PF | GE Anti-Island 4a.vi | 0250 06-17-15 11-00.tdms | 250 | 2015-06-17 18:01 | 2015-06-17 18:01 | 0.08485 | 0.107 | 0.02215 | 1697 | 1364 | 2140 | 2206 | 136 | 0.84486 | 60.6689 | 58.8091 | 63.2123 | 0.245
2 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 248-249 | 119.3 | 29.5 | y |  | 42 | 0.95 | 95.4 | 0.79966 | 53.4 | -8.212 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 c, 80%Pen, 0.95PF | GE Anti-Island 4a.vi | 0248 06-17-15 10-53.tdms | 248 | 2015-06-17 17:54 | 2015-06-17 17:54 | 0.1611 | 0.1054 | -0.0557 | 3222 | 2889 | 2108 | 2174 | 136
3 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 246-247 | 119.3 | 29.5 | y |  | 76 | 0.95 | 118.8 | 0.99581 | 42.8 | -8.212 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 b, 99%Pen, 0.95PF | GE Anti-Island 4a.vi | 0246 06-17-15 10-46.tdms | 246 | 2015-06-17 17:47 | 2015-06-17 17:47 | 0.0822 | 0.12085 | 0.03865 | 1644 | 1311 | 2417 | 2483 | 136 | 3.2017 | 63.3261 | 60.0744 | 72.133 | 1.0749
4 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 244-245 | 119.3 | 29.5 | y |  | 76 | 0.95 | 129.4 | 1.0847 | 53.4 | -8.212 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 c, 108%Pen, 0.95PF | GE Anti-Island 4a.vi | 0244 06-17-15 10-39.tdms | 244 | 2015-06-17 17:39 | 2015-06-17 17:39 | 0.06775 | 0.10655 | 0.0388 | 1355 | 1022 | 2131 | 2197 | 136 | 3.0136 | 62.8795 | 60.0452 | 71.6943 | 1.465
5 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | xoff b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 262-263 | 119.3 | 29.5 | y |  | 0 | 0.98 | 42.8 | 0.35876 | 42.8 | 6.7751 | 119.3 | n/a | 118.4 | 34.8 | Summer01, xoff b, 36%Pen, 0.98PF | GE Anti-Island 4a.vi | 0262 06-17-15 11-46.tdms | 262 | 2015-06-17 18:47 | 2015-06-17 18:47 | 0.0866 | 0.1418 | 0.0552 | 1732 | 1399 | 2836 | 2902 | 136 | 0.56988 | 60.0913 | 59.136 | 61.8262 | 1.1424
6 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 a | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 260-261 | 119.3 | 29.5 | y |  | 42 | 0.98 | 73.2 | 0.61358 | 31.2 | 6.7751 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 a, 61%Pen, 0.98PF | GE Anti-Island 4a.vi | 0260 06-17-15 11-40.tdms | 260 | 2015-06-17 18:40 | 2015-06-17 18:40 | 0.085 | 0.16815 | 0.08315 | 1700 | 1367 | 3363 | 3429 | 136 | 0.32172 | 60.3782 | 59.8224 | 61.8507 | 1.1655
7 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 258-259 | 119.3 | 29.5 | y |  | 42 | 0.98 | 95.4 | 0.79966 | 53.4 | 6.7751 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 c, 80%Pen, 0.98PF | GE Anti-Island 4a.vi | 0258 06-17-15 11-33.tdms | 258 | 2015-06-17 18:33 | 2015-06-17 18:33 | 0.1341 | 0.2048 | 0.0707 | 2682 | 2349 | 4096 | 4162 | 136 | 0.80452 | 60.7392 | 59.8048 | 64.6079 | 2.5694
8 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 256-257 | 119.3 | 29.5 | y |  | 76 | 0.98 | 118.8 | 0.99581 | 42.8 | 6.7751 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 b, 99%Pen, 0.98PF | GE Anti-Island 4a.vi | 0256 06-17-15 11-26.tdms | 256 | 2015-06-17 18:26 | 2015-06-17 18:26 | 0.08115 | 0.1934 | 0.11225 | 1623 | 1290 | 3868 | 3934 | 136 | 0.27321 | 60.4307 | 59.53 | 61.4182 | 0.37466
9 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 254-255 | 119.3 | 29.5 | y |  | 76 | 0.98 | 129.4 | 1.0847 | 53.4 | 6.7751 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 c, 108%Pen, 0.98PF | GE Anti-Island 4a.vi | 0254 06-17-15 11-19.tdms | 254 | 2015-06-17 18:19 | 2015-06-17 18:19 | 0.08 | 0.1472 | 0.0672 | 1600 | 1267 | 2944 | 3010 | 136 | 0.59121 | 60.3397 | 59.007 | 61.5067 | -0.29144
10 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | xoff b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 274-275 | 119.3 | 29.5 | y |  | 0 | 1 | 42.8 | 0.35876 | 42.8 | 31 | 119.3 | n/a | 118.4 | 34.8 | Summer01, xoff b, 36%Pen, 1.0PF | GE Anti-Island 4a.vi | 0274 06-17-15 12-41.tdms | 274 | 2015-06-17 19:41 | 2015-06-17 19:41 | 0.08275 | 0.1291 | 0.04635 | 1655 | 1322 | 2582 | 2648 | 136 | 0.30213 | 59.4654 | 58.8688 | 60.1117 | -0.0461
11 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 a | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 272-273 | 119.3 | 29.5 | y |  | 42 | 1 | 73.2 | 0.61358 | 31.2 | 31 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 a, 61%Pen, 1.0PF | GE Anti-Island 4a.vi | 0272 06-17-15 12-29.tdms | 272 | 2015-06-17 19:29 | 2015-06-17 19:29 | 0.06855 | 0.1666 | 0.09805 | 1371 | 1038 | 3332 | 3398 | 136 | 0.64112 | 60.376 | 59.4983 | 62.4267 | 1.4307
12 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 269-271 | 119.3 | 29.5 | y |  | 42 | 1 | 95.4 | 0.79966 | 53.4 | 31 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 c, 80%Pen, 1.0PF | GE Anti-Island 4a.vi | 0269 06-17-15 12-22.tdms | 269 | 2015-06-17 19:22 | 2015-06-17 19:23 | 0.10385 | 0.23695 | 0.1331 | 2077 | 1744 | 4739 | 4805 | 136 | 0.32942 | 59.9451 | 59.3179 | 61.0364 | 1.1474
13 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 266-268 | 119.3 | 29.5 | y |  | 76 | 1 | 118.8 | 0.99581 | 42.8 | 31 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 b, 99%Pen, 1.0PF | GE Anti-Island 4a.vi | 0266 06-17-15 12-15.tdms | 266 | 2015-06-17 19:15 | 2015-06-17 19:15 | 0.0074 | 0.403 | 0.3956 | 148 | 0 | 8060 | 8126 | 136 | 1.8011 | 60.4262 | 59.2282 | 84.9236 | 10.7449
14 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 264-265 | 119.3 | 29.5 | y |  | 76 | 1 | 129.4 | 1.0847 | 53.4 | 31 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 c, 108%Pen, 1.0PF | GE Anti-Island 4a.vi | 0264 06-17-15 12-08.tdms | 264 | 2015-06-17 19:08 | 2015-06-17 19:08 | 0.03735 | 0.3048 | 0.26745 | 747 | 414 | 6096 | 6162 | 136 | 0.27745 | 60.2855 | 59.3198 | 61.0455 | -0.38334
15 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | xoff b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 284-285 | 119.3 | 29.5 | y |  | 0 | 0.98 | 42.8 | 0.35876 | 42.8 | 55.2249 | 119.3 | n/a | 118.4 | 34.8 | Summer01, xoff b, 36%Pen, 0.98PF cap | GE Anti-Island 4a.vi | 0284 06-17-15 13-33.tdms | 284 | 2015-06-17 20:34 | 2015-06-17 20:34 | 0.0698 | 0.11085 | 0.04105 | 1396 | 1063 | 2217 | 2283 | 136 | 0.3031 | 58.9863 | 58.3319 | 59.7966 | 0.35099
16 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 a | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 282-283 | 119.3 | 29.5 | y |  | 42 | 0.98 | 73.2 | 0.61358 | 31.2 | 55.2249 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x45 a, 61%Pen, 0.98PF cap | GE Anti-Island 4a.vi | 0282 06-17-15 13-22.tdms | 282 | 2015-06-17 20:23 | 2015-06-17 20:23 | 0.15465 | 0.1533 | -0.00135 | 3093 | 2760 | 3066 | 3132 | 136
17 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x45 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 280-281 | 119.3 | 29.5 | y |  | 42 | 0.98 | 95.4 | 0.79966 | 53.4 | 55.2249 | 119.3 | n/a | 118.4 | 34.8 | n/a | n/a | n/a | n/a | [9 empty] | -1
18 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 b | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 278-279 | 119.3 | 29.5 | y |  | 76 | 0.98 | 118.8 | 0.99581 | 42.8 | 55.2249 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 b, 99%Pen, 0.98PF cap | GE Anti-Island 4a.vi | 0278 06-17-15 13-04.tdms | 278 | 2015-06-17 20:04 | 2015-06-17 20:04 | 0.00295 | 0.12495 | 0.122 | 59 | 0 | 2499 | 2565 | 72 | 0.19836 | 59.8719 | 58.9125 | 60.2498 | -1.0482
19 |  | 0.0,0.1,0.0,0.3,0.1,0.2,0.0 | x100 c | 20150617S01 | TestLogSummer01.xlsx | 113 | 31 | 276-277 | 119.3 | 29.5 | y |  | 76 | 0.98 | 129.4 | 1.0847 | 53.4 | 55.2249 | 119.3 | n/a | 118.4 | 34.8 | Summer01, x100 c, 108%Pen, 0.98PF cap | GE Anti-Island 4a.vi | 0276 06-17-15 12-51.tdms | 276 | 2015-06-17 19:52 | 2015-06-17 19:52 | 0.01935 | 0.26875 | 0.2494 | 387 | 54 | 5375 | 5441 | 136 | 0.4396 | 59.6403 | 58.4261 | 61.6439 | -1.1293